## Sheet1
FAN PERORMANCE CURVES 11" DIA FAN
Stactic Pressure |  | Airflow |  | Current Inout
mm H2O | Inches H2O | m3/h | CFM | Amps
0 | 0 | 1630 | 962 | 9.1
2.5 | 0.1 | 1500 | 885 | 9.3
5 | 0.2 | 1360 | 803 | 9.4
7.5 | 0.3 | 1150 | 679 | 9.2
10 | 0.4 | 920 | 543 | 8.9
12.5 | 0.5 | 630 | 372 | 9
15 | 0.6 | 390 | 230 | 9.2
CONDENSER PERFORMANCE
Heat rejection= 13475 BTU/hr
Air side pressure drop= 0.11 inH2O
178.87 inch cubed face area
Test Conditions
Ambient : 100°F
Inlet Refrig Temp: 200°F
Inlet pressure: 254 PSI
Subcooling: 10°F
Air Velocity: 400FPM
Refrigerant: R134